# CPCPFS3040 Conduct basic functional testing of water-based fire-suppression systems

Release: 2

CPCPFS3040 Conduct basic functional testing of water-based fire-suppression systems

# Modification History

| Release 2 | This version first released with CPC Construction, Plumbing and Services Training Package Release 5.1. Changes to Elements and Performance Criteria 1.1, 2.1, 3.5 and 3.8. |
| --- | --- |
| Release 1 | This version first released with CPC Construction, Plumbing and Services Training Package Release 5.0. Supersedes and is equivalent to CPCPFS3040A Conduct basic functional testing of water-based fire suppression systems. Updated to meet the Standards for Training Packages 2012. |

# Application

This unit specifies the skills and knowledge required to complete monthly and six-monthly routine service procedures on water-based fire suppression systems according to AS 1851 Routine service of fire protection systems and equipment in new or existing residential or commercial structures.

In some jurisdictions, this unit of competency may form part of accreditation, licensing, legislative, regulatory or certification requirements.

# Pre-requisite Unit

Nil.

# Unit Sector

Plumbing

# Elements and Performance Criteria

| Elements describe the essential outcomes. |  | Performance criteria describe what needs to be done to demonstrate achievement of the element. |  |
| --- | --- | --- | --- |
| 1 | Plan and apply compliance requirements to service operations. | 1.1 | Determine current legislative and industry requirements against organisational service operations and adjust as required to ensure compliance. |
|  |  | 1.2 | Interpret and follow the requirements of section one of AS 1851 Routine service of fire protection systems and equipment. |
|  |  | 1.3 | Identify and apply workplace policies and procedures, work health and safety (WHS) and environmental requirements. |
|  |  | 1.4 | Prepare for functional testing of water-based fire-suppression systems according to identified requirements. |
| 2 | Conduct monthly and six-monthly routine service inspections and record results. | 2.1 | Notify appropriate site contact of entry and follow site procedures for notifying occupants and/or staff of planned fire sprinkler system test. |
|  |  | 2.2 | Apply appropriate workplace procedures and risk control measures when inspecting water-based fire-suppression systems. |
|  |  | 2.3 | Identify plant and other system interfaces that must be isolated to allow for inspection activities. |
|  |  | 2.4 | Identify key control valves and determine their functions with reference to manufacturer instructions to allow for routine inspection activities. |
|  |  | 2.5 | Perform and record visual inspections and results according to AS 1851 Routine service of fire protection systems and equipment. |
| 3 | Conduct monthly and six-monthly testing and record results. | 3.1 | Implement test methods for monthly and six-monthly testing. |
|  |  | 3.2 | Perform routine testing procedures according to the required frequency schedule determined by AS 1851 Routine service of fire protection systems and equipment to verify the system functions as intended. |
|  |  | 3.3 | Compare test results with manufacturer, legislative and industry requirements. |
|  |  | 3.4 | Document results in accordance with AS 1851 Routine service of fire protection systems and equipment. |
|  |  | 3.5 | Identify, record and report any defects or non-conformances in accordance with AS 1851 Routine service of fire protection systems and equipment. |
|  |  | 3.6 | Prepare and forward reports to relevant persons for action. |
|  |  | 3.7 | Reinstate system according to organisational and manufacturer requirements. |
|  |  | 3.8 | Notify site contact of completion of test and follow site procedures for notifying occupants and staff. |
| 4 | Clean up. | 4.1 | Clear the work area, and dispose of, reuse or recycle materials in accordance with state and territory legislation and workplace policies and procedures. |
|  |  | 4.2 | Clean tools and equipment, check for serviceability and report any damage, and store and secure according to workplace procedures. |

# Foundation Skills

Foundation skills essential to performance are explicit in the performance criteria of this unit of competency.

# Unit Mapping Information

Supersedes and is equivalent to CPCPFS3040A Conduct basic functional testing of water-based fire suppression systems.

# Links

Companion volumes to this training package are available at the VETNet website - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=7e15fa6a-68b8-4097-b099-030a5569b1ad

Assessment Requirements for CPCPFS3040 Conduct basic functional testing of water-based fire-suppression systems

# Modification History

| Release 2 | This version first released with CPC Construction, Plumbing and Services Training Package Release 5.1. Changes to Elements and Performance Criteria 1.1, 2.1, 3.5 and 3.8. |
| --- | --- |
| Release 1 | This version first released with CPC Construction, Plumbing and Services Training Package Release 5.0. Supersedes and is equivalent to CPCPFS3040A Conduct basic functional testing of water-based fire suppression systems. Updated to meet the Standards for Training Packages 2012. |

# Performance Evidence

To demonstrate competency, a candidate must meet the performance criteria for this unit and must:

conduct inspections and perform routine services for three scheduled monthly activities and two scheduled six-monthly activities on:

two different wet systems

two different pre-action systems

two different deluge systems

perform six monthly tests to include:

main drain test and floor zone flow switch test, one manually operated and one solenoid operated on wet set

two different pre-action systems, including full trip test

include all of the following water-based fire-suppression systems:

deluge

wet or general system

residential system

combined sprinkler and hydrant system

double interlock pre-action

ensure all systems are interfaced to a fire indicator panel (FIP) and connected to alarm signalling equipment

comply with all relevant job plans and specifications, codes, Australian Standards, manufacturer’s specifications and jurisdictional requirements.

complete reports and work according to customer and organisational expectations within accepted timeframes.

# Knowledge Evidence

To be competent in this unit, a person must demonstrate knowledge of:

the basic principles of operation and purpose of components of water-based fire suppression systems:

accelerators and exhausters

alarm ‘dry’ (i.e. deluge) control valve assembly components

alarm ‘wet’ control valve assembly components

batteries

circulation and system pressure relief valves

isolation and control valves

pressure and flow switches

pressure gauges

pump controllers and ancillary equipment for control and indication

pumpsets

retard chambers

solenoid valves

sprinkler heads

system block plans

system pressure gauge schedules

water motor alarm gong

water supply tanks: atmospheric and suction with priming tanks

the general operation of water-based systems

the general operation of a gauge

the key features of legislation, regulations and codes applicable to inspecting and testing water-based fire-suppression systems

metric and imperial pressure gauge readings

systems and components of water-based fire-suppression systems:

air compressors fitted to systems

circulation and system pressure relief valves

controls on the pumpset controller panel:

fuel gauges

indicators

main isolating switch

flow switches and associated testing equipment

isolating valves associated with water-based fire-suppression system

main water supply underground key-operated valve location

pressure gauges

pumpsets associated with water-based fire-suppression system

pump starting switches

suction inlet strainers or screen on a static water supply for the water-based fire-suppression system

system block plan requirements for design details of systems installed since 1972

system main alarm bell and/or alarm strobe indicating building entry point for emergency personnel

system pressure gauge schedules, where required

system pressure maintenance or jacking pumps

water-based fire-suppression system control and alarm valves and ancillary equipment for control and alarm operation indication/interface

water supply tanks, water level indicators and automatic inflow valves

key control valves which may include those specified in AS 2118 Automatic fire sprinkler systems installed in:

associated control valve trim

activation small bore pipework to the alarm and control valve assembly

terminology used in relation to water-based fire-suppression systems

types of water supply tanks:

atmospheric

suction with priming

applications of water-based systems

water-based fire-suppression systems:

alternate wet or dry systems

combined sprinkler or hydrant systems

deluge systems

dry systems

pre-action and double interlock pre-action systems

residential and domestic systems

tail-end systems

wet and general systems

legislative and industry requirements:

dangerous goods regulations

licensing arrangements

environmental regulations

work health and safety (WHS) legislation, regulations and codes

relevant Commonwealth and state or territory building acts, regulations and codes, such as National Construction Code (NCC)

AS 1851 Routine service of fire protection systems and equipment

other relevant legislation relating to fire suppression equipment

organisational requirements:

client-specific contractual requirements

documentation and information systems and processes

legal and organisational policies and guidelines, including personnel practices and guidelines outlining work roles, responsibilities and delegations

use of electronic job scheduling and communication devices

system interfaces:

flow switches

pressure switches

tamper switches

valve positioning switches

control and indicating equipment (CIE)

plant shutdowns

devices that operate signals between the water-based fire-suppression system and other services:

building heating, ventilation and air conditioning (HVAC) services

fire brigade monitoring providers

CIE

other life safety systems:

warning systems

fire indicator panel (FIP)

methods to apply sustainability principles and concepts

testing procedures for:

checking desiccant condition (air dryer or crystals, water separator bowl) and cleaning or replacing as required

checking oil level and visually assessing condition of oil on air compressor

routine service frequency schedules including reference to AS 1851 Routine service of fire protection systems and equipment schedules of work conducted at regular frequencies that relate to the work scope for weekly, monthly, and six-monthly inspection and testing schedules

how to access relevant information, including codes and standards

tools, materials and equipment used for testing and maintaining water-based fire-suppression systems

WHS requirements for testing and maintaining water-based fire-suppression systems

installation requirements for water-based fire-suppression systems.

# Assessment Conditions

Assessors must satisfy the requirements for assessors listed in the Standards for Registered Training Organisations.

This unit must be assessed in the workplace or a close simulation using realistic workplace conditions, materials, activities, responsibilities, procedures, safety requirements and environmental considerations.

# Links

Companion volumes to this training package are available at the VETNet website - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=7e15fa6a-68b8-4097-b099-030a5569b1ad