# Assessment Requirements for CPCPFS3042 Conduct annual routine service of complex water-based fire-suppression systems

Release: 2

Assessment Requirements for CPCPFS3042 Conduct annual routine service of complex water-based fire-suppression systems

# Modification History

| Release 2 | This version first released with CPC Construction, Plumbing and Services Training Package Release 5.1. Changes to Elements and Performance Criteria 1.3, 2.1, and 2.2. |
| --- | --- |
| Release 1 | This version first released with CPC Construction, Plumbing and Services Training Package Release 5.0. Supersedes and is equivalent to CPCPFS3042A Conduct annual functional testing of complex water-based fire-suppression systems. Updated to meet the Standards for Training Packages 2012. |

# Performance Evidence

To demonstrate competency, a candidate must meet the performance criteria for this unit by:

conducting relevant an annual routine service (other than water flow testing) on water-based fire suppression systems with complex components for all the following systems:

a general sprinkler system with pumpset system

•	a combined sprinkler and hydrant systems

a deluge system

a pre-action system

a pressure reducing valve

a pressure relief valve

performing two installation and design surveys, one physical and one desktop survey (e.g. plans, specifications, photographic evidence, case studies) on a Class 2-9 building greater than 5000 square metres to produce an inspection report on the following elements:

pipework external condition

sprinkler head condition

sprinkler head obstructions

sprinkler head location and spacing

sprinkler head compatibility and ambient conditions (response time index (RTI) and sprinkler head and spray pattern)

external sprinkler requirements

design standard suitable for current building occupation requirements, such as classification and storage height.

# Knowledge Evidence

To be competent in this unit, a person must demonstrate knowledge of:

definitions of basic principles of operation and purpose of components of complex water-based fire protection systems

general operation of a gauge

general operation of complex water-based fire-suppression systems

metric and imperial pressure gauge readings

system components:

air compressors fitted to systems

circulation and system pressure relief valves

flow switches and associated testing equipment

isolating valves associated with water-based fire-suppression system

pressure gauges

pressure reducing equipment

pumpsets associated with water-based fire-suppression system

pump starting switches

purpose and key requirements of system block plan for installations installed since 1972

suction inlet strainers and screens on a static water supply for water-based fire-suppression system

system main alarm bell and/or alarm strobe indicating building entry point for emergency personnel

system pressure gauge schedules, where required

water-based fire-suppression system control and alarm valves and ancillary equipment for control and alarm operation indication/interface

water supply tanks, water level indicators and automatic inflow valves

water supply underground key-operated valve location

controls on the pumpset controller panel:

fuel gauges

indicators

main isolating switch

terminology used in relation to water-based fire-suppression systems

water-based fire-suppression system applications as defined in AS 2118 Automatic fire sprinkler systems or AS 2419 Fire hydrant installations \-- System design, installation and commissioning

legislative and industry requirements:

dangerous goods regulations

licensing arrangements

environmental regulations

work health and safety (WHS) legislation, regulations and codes

relevant Commonwealth and state or territory building acts, regulations and codes, such as National Construction Code (NCC)

AS 1851 Routine service of fire protection systems and equipment

organisational requirements, including:

client-specific contractual requirements

documentation and information systems and processes

legal and organisational policies and guidelines, including personnel practices and guidelines outlining work roles, responsibilities and delegations

use of electronic job scheduling and communication devices

system interfaces, including:

flow switches

pressure switches

tamper switches

valve positioning switches

devices that operate signals between the water-based fire-suppression system and other services such as:

building heating, ventilation and air conditioning (HVAC) services

fire brigade monitoring providers

other life safety systems, including:

warning systems

fire indicator panel (FIP)

applying inspections, tests and survey requirements to equipment and systems, according to relevant Australian standards, to determine that they are:

capable of operating as intended when originally installed

still suitable for the fire hazard or risk being protected, as no change in occupancy or use of the area protected has occurred since the equipment or system was installed or last modified

providing the coverage and protection needed to meet original design and performance requirements

reviewing documentation to verify that installed systems comply with legislative and industry requirements such as:

building’s essential services or fire safety measures listing

annual routine service, inspection, testing and surveying as referred to in AS 1851 Routine service of fire protection systems and equipment, including:

annual frequency inspection, testing and surveying activities, except water flow proving testing

operating pressure reducing valves to verify operation is at required pressures

operating pressure relief valves to verify operation is at required pressures

operating accelerator/exhauster and double interlock valves to verify operation is at required pressures and delivery time on dry pipe or pre-action systems

complex components of a water-based fire-suppression systems, including:

double interlock systems

pressure reducing systems

accelerator/exhauster systems

key control valves which may include those specified in AS 2118 Automatic fire sprinkler systems installed in:

associated control valve trim

activation small bore pipework to the alarm and control valve assembly

water-based fire-suppression systems, including:

alternate wet or dry systems

combined sprinkler or hydrant systems

deluge systems

dry systems

pre-action or recycle systems

residential and domestic systems

tail-end systems

installation and design survey information which may include the annual survey required by AS 1851 Routine service of fire protection systems and equipment, to determine that water-based fire-suppression systems design and installation are not impaired by changes to:

building structure

occupant use

environment

installation and design surveys conducted from floor level to identify design standard suitable for current building occupation requirements:

building classification

storage heights

external sprinkler requirements

pipework corrosion or damage

installation and design surveys conducted from floor level to identify design standard suitable for current building occupation:

sprinkler head requirements

compatibility and ambient conditions

head condition

head location and spacing

head obstructions

spray pattern

temperature rating and RTI

methods of applying sustainability principles and concepts

testing procedures for:

checking desiccant condition (air dryer or crystals, water separator bowl) and cleaning or replacing as required

checking oil level and visually assessing condition of oil on air compressor

routine service frequency schedules:

reference to AS 1851 Routine service of fire protection systems and equipment schedules of work conducted at regular frequencies that relate to the work scope for weekly, monthly, and six-monthly inspection and testing activities

how to access relevant information, including codes and standards

tools, materials and equipment used for conducting routine services of complex water-based fire-suppression systems

WHS requirements for conducting routine services of complex water-based fire-suppression systems.

# Assessment Conditions

Assessors must satisfy the requirements for assessors listed in the Standards for Registered Training Organisations.

This unit must be assessed in the workplace or a close simulation using realistic workplace conditions, materials, activities, responsibilities, procedures, safety requirements and environmental considerations.

# Links

Companion volumes to this training package are available at the VETNet website - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=7e15fa6a-68b8-4097-b099-030a5569b1ad