# Assessment Requirements for CPCPFS3043 Conduct functional water flow testing

Release: 2

Assessment Requirements for CPCPFS3043 Conduct functional water flow testing

# Modification History

| Release 2 | This version first released with CPC Construction, Plumbing and Services Training Package Release 5.1. Typographical error corrected in Element 1.6. |
| --- | --- |
| Release 1 | This version first released with CPC Construction, Plumbing and Services Training Package Release 5.0. Supersedes and is equivalent to CPCPFS3043A Conduct functional water flow testing. Updated to meet the Standards for Training Packages 2012. |

# Performance Evidence

To demonstrate competency, a candidate must meet the performance criteria for this unit by:

conducting a load test on a wet and general electrical pumpset according to AS 1851 Routine service of fire protection systems and equipment

conducting a load test on a wet and general diesel pumpset according to AS 1851 Routine service of fire protection systems and equipment

conducting a functional water-flow test on a hydrant system incorporating a pumpset

conducting two functional water-flow tests on a hydrant system:

one with a portable flow meter

one connected by a length of fire hose.

# Knowledge Evidence

To be competent in this unit, a person must demonstrate knowledge of:

basic principles of hydraulics

basic principles of operation and purpose of components of a water-based fire protection system:

deluge control valve assembly components

alarm wet control valve assembly components

booster valve assembly

circulation and system pressure relief valves

compression ignition engine governing controls

differential pressure gauges

hand tachometers

hydrant landing valve assembly

isolation and control valves

manometers

orifice plates

pitot tube water flow test instrument

pressure and flow switches

pressure gauges

pump controllers and ancillary equipment for control and indication

pumpsets

solenoid valves

system block plans

system pressure gauge schedules

throttling valves

ultrasonic flow measuring equipment

ultrasonic thickness gauges

venturi devices

water supply tanks (atmospheric, pressure and suction with priming tanks)

general operation of a pumpset:

compression ignition engine governing control devices

cooling systems

design speed requirements

exhaust systems

fuel systems

full load operation

normal running operation

pre-start and post-start checks

pumpset performance curve

pumpset controllers

starting and stopping methods

suction and discharge connections and pressures readings

general operation of water-based fire-suppression systems

terminology used in relation to water-based fire-suppression systems

water-based fire-suppression system components:

air compressors fitted to control valves

circulation and system pressure relief valves

electric motor specification plate

flow switches and associated testing equipment

isolating valves associated with water-based fire-suppression system

mains water supply underground key-operated valve location

most hydraulically disadvantaged testing point on a system hose reel and hydrant system

pressure gauges

pumpsets associated with water-based fire-suppression systems

pump starting switches

suction inlet strainers or screen on a static water supply for water-based fire-suppression system

system block plans

system main alarm bell or alarm strobe indicating building entry point for emergency personnel

system pressure gauge schedules

water supply tanks, water level indicators and automatic inflow valves

water-based fire-suppression system control and alarm valves and ancillary equipment for control and alarm operation indication or interface

controls on the pumpset controller panel:

fuel gauges

indicators

main isolating switch

water-based fire-suppression system applications as defined in AS 2118 Automatic fire sprinkler systems

legislative and industry requirements:

relevant Commonwealth and state or territory building acts, regulations and codes, such as the National Construction Code (NCC)

AS 1851 Routine service of fire protection systems and equipment

relevant legislation relating to testing of fire protection equipment

organisational requirements:

client-specific contractual requirements

documentation and information systems and processes

legal and organisational policies and guidelines, including personnel practices and guidelines outlining work roles, responsibilities and delegations

using electronic job scheduling and communication devices

commissioning tests detailed in relevant Australian standards and manufacturers documentation to verify performance of an installed, repaired or altered piece of equipment or system

checking for compliance including applying inspections, tests and survey requirements to equipment and systems according to relevant Australian standards to determine that they are:

capable of operating as intended when originally installed

still suitable for the fire hazard or risk being protected as no change in occupancy or use of the area protected has occurred since the equipment or system was installed or last modified

providing the coverage and protection needed to meet original design and performance requirements

checking for compliance, including reviewing documentation to verify that installed systems comply with legislative and industry requirements such as:

buildings essential services or fire safety measures listing

relevant Commonwealth and state or territory building acts, regulations and codes

relevant Australian standards listed on essential service listing

environmental regulations

water-based fire-suppression systems as defined in AS 2118 Automatic fire sprinkler systems and AS 2419 Fire hydrant installations:

combined sprinkler and hydrant systems

deluge systems

dry systems

hydrant systems

pre-action or recycle systems

residential and domestic systems

tail-end systems

specific locations where test equipment can be attached to measure and record water flow and pressure to meet legislative and industry requirements

water flow test equipment:

differential pressure gauges

hand tachometers

manometers

orifice plates

pitot tube water flow test instrument

ultrasonic flow measuring equipment

ultrasonic thickness gauges

venturi devices

system interface components such as flow, pressure, tamper and valve positioning switches that operate signals between the water-based fire-suppression system and other services such as:

building heating, ventilation and air conditioning (HVAC) services

fire brigade monitoring providers

other life safety systems:

warning systems

fire indicator panel (FIP)

methods of applying sustainability principles and concepts

routine service frequency schedules:

reference to AS 1851 Routine service of fire protection systems and equipment schedules of work conducted at regular frequencies that relate to the work scope for weekly, monthly, and six-monthly inspection and testing activities

how to access relevant information, including codes and standards

tools, materials and equipment used for conducting functional water flow testing

work health and safety (WHS) requirements for conducting functional water flow testing.

# Assessment Conditions

Assessors must satisfy the requirements for assessors listed in the Standards for Registered Training Organisations.

This unit must be assessed in the workplace or a close simulation using realistic workplace conditions, materials, activities, responsibilities, procedures, safety requirements and environmental considerations.

# Links

Companion volumes to this training package are available at the VETNet website - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=7e15fa6a-68b8-4097-b099-030a5569b1ad