# Assessment Requirements for CPCPPS5033 Design vacuum drainage systems

Release: 3

Assessment Requirements for CPCPPS5033 Design vacuum drainage systems

# Modification History

| Release 2 | This version first released with CPC Construction, Plumbing and Services Training Package Release 6.2. Removed duplicated heading from Performance Evidence. |
| --- | --- |
| Release 1 | This version first released with CPC Construction, Plumbing and Services Training Package Release 5.0. Supersedes and is equivalent to CPCPPS5033A Design vacuum sewerage systems. Updated to meet the Standards for Training Packages 2012. |

# Performance Evidence

To demonstrate competency, a candidate must meet the performance criteria for this unit by:

designing, sizing and documenting the installation and layout details for a vacuum infrastructure sewer system for:

a residential development of 50 properties incorporating:

vacuum sewage collection chambers

vacuum sewer mains

vacuum pump station

pump rising main

ventilation

odour control

a high-rise mixed development building, to a minimum of 29 floors, inclusive of a basement, to include fixtures on each floor level, incorporating:

vacuum pump station

vacuum sanitary drainage system

pump rising main

ventilation

odour control

applying sustainability principles and concepts throughout to achieve a star rating under the Green Building Council of Australia rating scheme

evaluating and documenting design parameters, including client, regulatory and manufacturer requirements and relevant Australian Standards and codes complex sanitary plumbing and drainage systems

evaluating health risks associated with the sanitary plumbing and drainage system

selecting materials and components for compliance, fitness for purpose, durability, compatibility and cost-effectiveness.

# Knowledge Evidence

To be competent in this unit, a candidate must demonstrate knowledge of:

common terminology and definitions used in the design of vacuum drainage systems

application of statutory and regulatory requirements and relevant Australian Standards and codes including:

Acts, regulations and Commonwealth, state or territory and local government policies

AS/NZ 3500 National plumbing and drainage

AS 2200 Design charts for water supply and sewerage

Environmental Protection Authority (EPA)

National Construction Code (NCC)

Sewerage Code of Australia

other relevant Australian Standards and codes

scope of work requirements:

interpreting plans and specifications

sizing and documenting layout of vacuum drainage systems including residential, commercial and industrial

design requirements:

acoustic performance

architectural plans

building specifications

fire safety requirements

flow requirements and sizing of pipework

odour control

owner requirements

pipework identification

Sewerage Code of Australia

vacuum pumping station

ventilation requirements

cost-benefit analysis comparing suitable materials and system choices available to enable cost-effective choices without compromising the integrity of the project

nature of materials used and effects of performance under various conditions:

copper (Cu)

polyethylene (PE)

polypropylene (PP)

polyvinyl chloride (PVC)

stainless steel

other approved material

manufacturer requirements:

material specifications

collection and storage systems

design and installation

equipment installation

pump installation

selection of compatible sanitary fixtures

technical manuals

manufacturer specifications, including hazards identified in relation to devices and systems used

information required to conduct a desktop study to outline design parameters:

architectural and building plans

developer plans

manufacturer data

other documents relevant to designing vacuum sewerage systems

characteristics and application of different jointing methods

vacuum drainage system attributes:

availability

cost

flexibility

installation requirements

low water usage

risks

vacuum loading units (VLU)

site conditions

performance requirements of vacuum drainage system:

discharge requirements

durability

emergency storage and/or power backup

longevity

self-cleaning ability

sufficient capacity

layout of pipework systems:

sewer infrastructure systems:

cover

grade

location of vacuum pump station

location of vacuum sewage collection chambers

odour control

pipe access

ventilation

high-rise building projects:

acoustic performance

amenity of the building

clipping and pipe support

location of pipework (fire rating of enclosure)

function of the building

impingement on floor heights

materials to be used

size of penetrations

type of building structure

effect on building integrity and aesthetic appeal

principles of economy, serviceability, durability and fit fur use

installation requirements:

acoustic performance

bedding

pipe protection:

cover

corrosion

impact

grade

level of workmanship

fire rating

manufacturer-recommended specific fixings

pipe support

provision for pipe movement

serviceability and access

pipe size calculations including:

determining flow and fixture loadings

equivalent population (EP) density

calculating gradient

interpreting design charts and tables

determining self-cleaning velocities

manufacturer requirement

probable simultaneous demand

uses and limitations for pipe supports:

bedding

bracket spacing

concrete support

corrosion protection

cover

hanging brackets

manufacturer-recommended specific fixings

material requirements

provision for expansion

thrust blocks

wall and ceiling brackets

vacuum pumping station and pump control requirements:

access covers

automatic controls

capacity

corrosion-resistant materials

detailing

emergency storage

emergency power supply

high and low-level water controls and alarms

impeller sizing

inlet and outlet design requirements

installation and mounting requirements

macerator requirements

odour control

pneumatic control switch assembly

pump selection

pump sizing

pump well sizing

space requirements

vacuum pump systems

valve requirements

ventilation

warning system

characteristics and application of different fittings, valves and controls:

fittings:

bends

elbows

inspection and maintenance access

tees

unions

valves:

backflow prevention

isolating

non-return

strainers

vacuum diaphragm valve

controls:

pneumatic control switch assembly

vacuum pressure sensing

motorised actuated valves

vacuum management system

the use and limitations of computer software packages including manufacturer and proprietary design software

plans and specifications requirements:

plans:

axonometrics

cross-sections

details

elevations

isometrics

schematics

site

sections

specifications:

access chambers (manholes)

bedding

commissioning

concrete support and detailing specialised components

jointing

manufacturer requirements

materials

odour control

pump rising main

work health and safety (WHS)

selection of compatible vacuum sanitary fixtures

support

testing

vacuum pump station

vacuum drainage collection chambers

vacuum sewer mains

ventilation

workmanship

testing methods:

compressed air test

flow testing

hydrostatic test

inspection checklist

performance

vacuum

quality assurance (QA) audit

commissioning schedule requirements:

system certification

check for foreign material

leak check

emergency procedures

system defects

system functions as per design

operation and maintenance manual requirements:

as installed drawings

results of commissioning test

certification documentation

maintenance schedules

manufacturer brochures and technical information

operating procedures

sustainability principles and concepts:

selecting appropriate material to ensure minimal environmental impact

efficient use of material

efficient energy usage/capital outlay comparison

positive effect on the environment in regard to no potential overflow or leakage

water efficient

consideration of the Green Building Council of Australia rating scheme

local environment consideration overflow disposal/reuse.

# Assessment Conditions

Assessors must meet the requirements for assessors contained in the Standards for Registered Training Organisations.

This unit must be assessed in the workplace or a close simulation using realistic workplace conditions, materials, activities, responsibilities, procedures, safety requirements and environmental considerations.

# Links

Companion volumes to this training package are available at the VETNet website - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=7e15fa6a-68b8-4097-b099-030a5569b1ad