# CPPFES2047 Inspect and test control and indicating equipment

Release: 1

CPPFES2047 Inspect and test control and indicating equipment

# Modification History

| Release 1 | This version first released with CPP Property Services Training Package Release 13.0. Supersedes and is equivalent to CPPFES2047A Inspect and test control and indicating equipment. Updated to meet the Standards for Training Packages 2012. |
| --- | --- |

# Application

This unit of competency specifies the skills and knowledge required to complete routine monthly and six-monthly inspection and testing procedures to verify that control and indicating equipment (CIE) for a fire alarm system functions as intended. It includes working safely, isolating and resetting CIE, conducting compliance tests, visually inspecting, identifying non-compliance defects, and fulfilling mandatory reporting requirement. Service activities are conducted in compliance with requirements of the relevant Australian Standards and National Construction Code (NCC).

The skills and knowledge described in this unit do not require an electrical licence or an Australian Communications and Media Authority (ACMA) cabling licence to practise. The unit does not cover any installation, replacement, maintenance or repair functions that are restricted to licensed trades or occupations.

The unit is suitable for those with basic skills and knowledge undertaking routine work tasks under the direction of more experienced workers.

Ozone depleting substances (ODS) and synthetic greenhouse gases (SGG) are gaseous fire-extinguishing agents listed in Schedule 1 of the Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 and by law, can only be handled by people who hold an appropriate extinguishing agent handling licence (EAHL). This unit supports one or more EAHLs prescribed under the Act. For further information, check with the relevant regulatory authority.

# Pre-requisite Unit

Nil.

# Unit Sector

Fire Protection Inspection and Testing

# Elements and Performance Criteria

| Elements describe the essential outcomes. |  | Performance criteria describe what needs to be done to demonstrate achievement of the element. |  |
| --- | --- | --- | --- |
| 1 | Plan and prepare for service operation. | 1.1 | Read work instructions, installation drawings and specifications to clarify service timeframes, client needs, and location of system components and materials. |
|  |  | 1.2 | Discuss planned service procedures with relevant persons to clarify client needs and expectations. |
|  |  | 1.3 | Plan work activities to prevent ODS and SGG emissions and comply with relevant Australian Standards, NCC, regulations, work health and safety (WHS) and workplace requirements. |
|  |  | 1.4 | Arrange inspection and test procedures to suit CIE according to manufacturer, regulatory and workplace requirements. |
|  |  | 1.5 | Confirm and access documentation required to conduct tests to meet regulatory and workplace requirements. |
|  |  | 1.6 | Select, check and use required test devices, tools and equipment, including personal protective equipment (PPE). |
|  |  | 1.7 | Arrange access to worksite and communicate with responsible entity and affected persons to advise duration and impact of planned service procedures and to ensure alternative safety arrangements are implemented. |
|  |  | 1.8 | Prepare to follow ODS, SGG and WHS policies and procedures and apply required risk control measures when inspecting and testing CIE. |
| 2 | Inspect CIE. | 2.1 | Identify CIE functions to be used to conduct routine tests according to manufacturer requirements and relevant maintenance schedule. |
|  |  | 2.2 | Isolate alarm zone circuits, plant and other system interfaces to allow conduct of maintenance activities according to ODS, SGG and WHS policies and procedures. |
|  |  | 2.3 | Isolate circuits and actuators according to regulatory and workplace requirements. |
|  |  | 2.4 | Conduct visual inspection according to the monthly and six-monthly schedules of the relevant Australian Standard. |
|  |  | 2.5 | Validate CIE inspection results according to requirements of the relevant Australian Standard. |
| 3 | Test CIE. | 3.1 | Isolate circuits, actuators, back-to-base facilities and other system interfaces according to regulatory and workplace requirements. |
|  |  | 3.2 | Conduct checks to confirm alarm zone circuits, plant and other system interfaces are isolated and system cannot be activated during testing according to workplace requirements. |
|  |  | 3.3 | Conduct monthly and six-monthly tests according to the relevant Australian Standard. |
|  |  | 3.4 | Check CIE and components to verify functionality in accordance with manufacturer requirements and final design documentation. |
|  |  | 3.5 | Discuss methods for dealing with unexpected situations with relevant persons and, where required, obtain approval from authorised persons to deal safely with unexpected situations. |
|  |  | 3.6 | Record results of tests, discussions and actions taken according to regulatory and workplace requirements. |
| 4 | Finalise service operation. | 4.1 | Reset CIE and other interfaced equipment and verify system as fully operational with no alarms present. |
|  |  | 4.2 | Complete service documentation and report outstanding defects, non-compliances and recommended rectifications according to Australian Standards, regulatory and workplace requirements. |
|  |  | 4.3 | Check tools, equipment and test devices for faults, wear or damage and rectify or report problems according to workplace requirements. |
|  |  | 4.4 | Leave client premises in a safe, clean and tidy condition. |

# Foundation Skills

Foundation skills essential to performance are explicit in the performance criteria of this unit of competency.

# Unit Mapping Information

Supersedes and is equivalent to CPPFES2047A Inspect and test control and indicating equipment.

# Links

Companion volumes to this training package are available at the VETNet website - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=6f3f9672-30e8-4835-b348-205dfcf13d9b

Assessment Requirements for CPPFES2047 Inspect and test control and indicating equipment

# Modification History

| Release 1 | This version first released with CPP Property Services Training Package Release 13.0. Supersedes and is equivalent to CPPFES2047A Inspect and test control and indicating equipment. Updated to meet the Standards for Training Packages 2012. |
| --- | --- |

# Performance Evidence

To demonstrate competency, a candidate must meet the elements and performance criteria of this unit by inspecting and testing control and indicating equipment (CIE) installed across 10 different sites and specifically interfaced to different fire-suppression systems:

conventional fire indicating panels and microprocessor analogue fire indicating panel fire detection systems

fire alarm systems that comply with AS 1670.1 Fire detection, warning, control and intercom systems - Fire (or its successor)

emergency warning and intercommunication systems that comply with AS 1670.4 Fire detection, warning, control and intercom systems - System design, installation and commissioning—Emergency warning and intercom systems (or its successor)

fire alarm systems interfaced with activating mechanisms of a fire-suppression system.

# Knowledge Evidence

To be competent in this unit, a candidate must demonstrate knowledge of:

action to take when a breach of regulation, work health and safety (WHS), ozone depleting substances (ODS), synthetic greenhouse gases (SGG) or other policy occurs when inspecting and testing CIE

common controls and indicators on CIE

detection and warning components connected to CIE

environmental conditions that cause actuators to create false alarms

implications of not complying with regulatory requirements when inspecting and testing CIE

key features of legislation, regulations, codes and Australian Standards relevant to inspecting and testing CIE:

environment protection, ODS and SGG emission requirements

extinguishing agent handling licence (EAHL) requirements

intent of the Australian Standard for the maintenance of fire protection systems and equipment in relation to CIE inspect and test operations, and requirements of the monthly and six-monthly maintenance schedules relevant to conventional and addressable CIE

National Construction Code (NCC) and deemed-to-satisfy requirements

records and documentation

key functional differences between a conventional and addressable CIE

key operational principles of CIE specifically interfaced to fire-suppression systems

local controls (LC), local control stations (LCS), aural alarms, visual warning devices (VWD) and actuators on fire-suppression systems interfaced to CIE

operation of actuators

types, purpose of and safety requirements of tools, equipment and testing devices used when inspecting and testing CIE:

hand and power tools

personal protective equipment (PPE)

testing devices: barcode readers, safety equipment and simulator actuators

types of electrical safeguards used to protect persons and property when inspecting and testing CIE

workplace requirements for inspecting and testing CIE:

maintenance of tools, equipment and testing devices

WHS, including hazard and risk identification and control.

# Assessment Conditions

Assessors must meet the requirements for assessors contained in the Standards for Registered Training Organisations.

Assessment must be conducted in the workplace or a simulated workplace using realistic conditions, materials, activities, responsibilities, procedures, safety requirements and environmental considerations.

Candidates must have access to drawings, documentation, tools, equipment, testing devices and installed CIE required to achieve the performance evidence.

# Links

Companion volumes to this training package are available at the VETNet website - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=6f3f9672-30e8-4835-b348-205dfcf13d9b