# CPPFES2049 Conduct recovery, reclaim and fill operations for scheduled gaseous fire-extinguishing agents

Release: 1

CPPFES2049 Conduct recovery, reclaim and fill operations for scheduled gaseous fire-extinguishing agents

# Modification History

| Release 1 | This version first released with CPP Property Services Training Package Release 13.0. Supersedes and is equivalent to CPPFES2049A Conduct recovery, reclaim and fill operations for scheduled gaseous fire-extinguishing agents. Unit updated to meet the Standards for Training Packages 2012. |
| --- | --- |

# Application

This unit of competency specifies the skills and knowledge required to use processing equipment to recover and reclaim ozone depleting substances (ODS) and synthetic greenhouse gases (SGG), and fill ODS and SGG containers.

The unit is suitable for those with basic skills and knowledge undertaking routine work tasks under the direction of more experienced workers.

ODS and SGG are gaseous fire-extinguishing agents listed in Schedule 1 of the Ozone Protection and Synthetic Greenhouse Gas Management Act 1989 and by law, can only be handled by people who hold an appropriate extinguishing agent handling licence (EAHL). This unit supports one or more EAHLs prescribed under the Act. For further information, check with the relevant regulatory authority.

# Pre-requisite Unit

Nil.

# Unit Sector

Fire Protection Inspection and Testing

# Elements and Performance Criteria

| Elements describe the essential outcomes. |  | Performance criteria describe what needs to be done to demonstrate achievement of the element. |  |
| --- | --- | --- | --- |
| 1 | Plan and prepare for ODS and SGG recovery. | 1.1 | Read work instructions to clarify types and processing requirements of ODS and SGG extinguishing agents and containers. |
|  |  | 1.2 | Plan work activities to prevent ODS and SGG emissions and comply with relevant Australian Standards, regulatory, work health and safety (WHS) and workplace requirements. |
|  |  | 1.3 | Identify potential and actual breaches of rules and regulations associated with work instructions and take required action to ensure compliance according to regulatory and workplace requirements. |
|  |  | 1.4 | Select and use required tools and equipment, including personal protective equipment (PPE). |
|  |  | 1.5 | Identify and prepare to control hazards in the work area according to workplace requirements. |
| 2 | Prepare processing equipment for operation. | 2.1 | Set up processing equipment according to manufacturer requirements. |
|  |  | 2.2 | Pressurise processing equipment and check to ensure line holds pressure. |
|  |  | 2.3 | Perform leak detection test on processing equipment and connections. |
|  |  | 2.4 | Replace or recycle connections, filters and hoses as required before commencing processing. |
|  |  | 2.5 | Check equipment set-up for correct operation and rectify or report defects according to workplace requirements. |
| 3 | Recover and reclaim ODS and SGG materials. | 3.1 | Identify types of ODS or SGG containers, valves, labels and transport caps, and select suitable method of recovery according to regulatory and workplace requirements. |
|  |  | 3.2 | Weigh containers and record mass before processing. |
|  |  | 3.3 | Check and confirm container connections to processing equipment. |
|  |  | 3.4 | Operate and monitor processing equipment and complete recovery processing according to manufacturer and workplace requirements. |
|  |  | 3.5 | Perform quality control analysis of recovered material, confirm acceptable results and activate reclamation processing equipment according to manufacturer and workplace requirements. |
|  |  | 3.6 | Monitor equipment operation and complete reclamation processing according to manufacturer and workplace requirements. |
|  |  | 3.7 | Weigh containers and record mass after processing. |
| 4 | Prepare container and assemble valve. | 4.1 | Select and gather containers and valve components to suit ODS or SGG extinguishing agent. |
|  |  | 4.2 | Assemble valve components and connect assembled valve to container. |
|  |  | 4.3 | Check containers and labels for fill processing to confirm accuracy. |
| 5 | Fill container and complete documentation. | 5.1 | Check and confirm container connection to processing equipment according to manufacturer requirements. |
|  |  | 5.2 | Operate and monitor processing equipment and complete fill process according to manufacturer and workplace requirements. |
|  |  | 5.3 | Weigh container to verify fill processing and record container mass. |
|  |  | 5.4 | Pressurise system container to standard for type of agent and container. |
|  |  | 5.5 | Evacuate transfer equipment lines. |
|  |  | 5.6 | Remove container from processing equipment, test for leaks and rectify or report defects according to regulatory and workplace requirements. |
|  |  | 5.7 | Prepare container for service and pack filled container according to regulatory and workplace requirements. |
|  |  | 5.8 | Complete service documentation detailing recovery, reclaim and fill results according to regulatory and workplace requirements. |

# Foundation Skills

Foundation skills essential to performance are explicit in the performance criteria of this unit of competency.

# Unit Mapping Information

Supersedes and is equivalent to CPPFES2049A Conduct recovery, reclaim and fill operations for scheduled gaseous fire-extinguishing agents.

# Links

Companion volumes to this training package are available at the VETNet website - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=6f3f9672-30e8-4835-b348-205dfcf13d9b

Assessment Requirements for CPPFES2049 Conduct recovery, reclaim and fill operations for scheduled gaseous fire-extinguishing agents

# Modification History

| Release 1 | This version first released with CPP Property Services Training Package Release 13.0. Supersedes and is equivalent to CPPFES2049A Conduct recovery, reclaim and fill operations for scheduled gaseous fire-extinguishing agents. Unit updated to meet the Standards for Training Packages 2012. |
| --- | --- |

# Performance Evidence

To demonstrate competency, a candidate must meet the elements and performance criteria of this unit by conducting recovery, reclaim and fill operations for scheduled gaseous fire-extinguishing agents on two different occasions.

# Knowledge Evidence

To be competent in this unit, a candidate must demonstrate knowledge of:

action to take when a breach of work health and safety (WHS), ozone depleting substances (ODS) and synthetic greenhouse gases (SGG) regulation or other policy occurs when conducting recovery, reclaim and fill operations for scheduled gaseous fire-extinguishing agents

documentation used during recovery, reclamation and fill processing of ODS and SGG containers

fill density requirements for different agents per unit of volume of container

implications of ignoring safety precautions used in recovery, reclamation and fill processing

key features of legislation, regulations, Australian Standards and licensing relevant to recovery, reclaim and fill operations for scheduled gaseous fire-extinguishing agents:

environmental protection, ODS and SGG emission requirements

extinguishing agent handling licence (EAHL) requirements

records and documentation

storing, recovering, recycling and charging scheduled ODS and SGG agents

manual-handling techniques and aids to move gaseous fire-extinguishing agent containers

maximum working pressure and water capacity of containers to determine container fill requirements

methods for:

leak detection testing

selecting correct valve and components to suit container and agent requirements

recovering and reclaiming ODS and SGG materials from containers

reasons and methods for preventing ODS and SGG emissions in the workplace

types of:

containers used for ODS and SGG materials

materials found in ODS and SGG containers

sealants suitable for different gaseous agents

transport caps, labels, numbers and codes used on containers containing ODS and SGG materials

types and purpose of tools and equipment used when recovering and reclaiming ODS and SGG extinguishing agents and filling containers:

leak detection devices

manual-handling aids

processing and pressurising equipment

personal protective equipment (PPE)

scales

workplace requirements for conducting recovery, reclaim and fill operations for scheduled gaseous fire-extinguishing agents:

maintenance of tools and equipment

WHS, including hazard and risk identification and control.

# Assessment Conditions

Assessors must meet the requirements for assessors contained in the Standards for Registered Training Organisations.

Assessment must be conducted in the workplace or a simulated workplace using realistic conditions, materials, activities, responsibilities, procedures, safety requirements and environmental considerations.

Candidates must have access to documentation, tools, equipment and containers required to achieve the performance evidence.

# Links

Companion volumes to this training package are available at the VETNet website - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=6f3f9672-30e8-4835-b348-205dfcf13d9b