# ICTCBL241 Terminate metallic conductor customer cable

Release: 1

ICTCBL241 Terminate metallic conductor customer cable

# Modification History

| Release | Comments |
| --- | --- |
| Release 1 | This version released with ICT Information and Communications Technology Training Package Version 5.0. |

# Application

This unit describes the skills and knowledge required to terminate metallic conductor cable or to join cable in a terminating block for a new cable installation or upgrade of cable capacity for an existing network or subsystem, or cabling infrastructure for convergence to next generation networks (NGNs).

It applies to individuals who work in technical roles carrying out indoor and outdoor, domestic, commercial or industrial installations for all communications applications, digital and analog, telephony, data, video, digital broadcasting, computer networks, local area networks (LANs), wide area networks (WANs) and multimedia.

Licensing, legislative, regulatory and certification requirements apply to telecommunications systems. All customer cabling work in the telecommunications, fire, security and data industries must be performed by a registered cabler. All cablers are required to register with an Australian Communications and Media Authority (ACMA) accredited registrar.

# Unit Sector

Telecommunications – Cabling

# Elements and Performance Criteria

| ELEMENT | PERFORMANCE CRITERIA |
| --- | --- |
| Elements describe the essential outcomes. | Performance criteria describe the performance needed to demonstrate achievement of the element. |
| 1. Prepare cable termination | 1.1 Access site according to customer and worksite requirements 1.2 Prepare for cable terminating work according to regulatory environment, cabling environment, cable type, cable identification, termination systems, earthing and protection, and records 1.3 Select correct termination tools and materials for installation 1.4 Notify appropriate personnel of identified safety hazards at cabling worksite 1.5 Identify remote power feeding services that operate at above telecommunications network voltage (TNV) inside customer premises 1.6 Contact customer where risks with remote power feed are identified 1.7 Remove all contaminants from worksite that may adversely affect termination and prepare worksite to ensure adequate visibility to minimise errors and to reduce eye strain 1.8 Design cable and block location within frame, with capacity for expansion where possible 1.9 Segregate incoming and outgoing cables for ease of access and to minimise overlaying and backtracking of cable |
| 2. Terminate cable | 2.1 Remove cable sheath to allow for conductor length and installation requirements 2.2 Fan out cable pair groups to manufacturer coding system to ensure correct terminating sequence and unique identification as required 2.3 Install over-voltage protection devices to all cables with metallic component as required 2.4 Install terminating modules to frame according to manufacturer specifications 2.5 Fan cable pairs neatly to termination equipment to facilitate accurate termination 2.6 Terminate cable using correct tool, according to work health and safety (WHS) and environmental requirements, and manufacturer specifications 2.7 Earth cable shield to manufacturer specifications and industry standards |
| 3. Test termination | 3.1 Conduct visual inspection to confirm termination colour code sequence has been followed 3.2 Test termination to satisfy performance specifications and record results as required |
| 4. Complete records and clean-up site | 4.1 Label cable pairs clearly to provide an accurate identification according to manufacturer specifications, industry standards and customer requirements 4.2 Update records and plans with cabling details to provide accurate record according to industry codes of practice and current Australian Standards 4.3 Complete telecommunications cabling advice (TCA) forms 4.4 Remove installation waste and debris from worksite and dispose of according to environmental requirements to maintain safe worksite conditions |

# Foundation Skills

This section describes those language, literacy, numeracy and employment skills that are essential to performance, but not explicit in the performance criteria.

| Skill | Description |
| --- | --- |
| Reading | Interprets textual information from relevant sources to identify relevant and key information |
| Writing | Uses clear, specific and industry related terminology to complete workplace documentation |
| Numeracy | Takes readings and measurements and interprets results |
| Navigate the world of work | Complies with explicit policies, procedures and legislative requirements relevant to own role |
| Interact with others | Identifies and follows accepted communication practices and protocols when liaising with customers, colleagues or supervisors |
| Get the work done | Determines job sequence and works logically and systematically to undertake clearly defined tasks Analyses task requirements to decide on appropriate equipment and practices |

# Unit Mapping Information

ICTCBL241 Terminate metallic conductor customer cable supersedes and is equivalent to ICTCBL203 Terminate metallic conductor customer cable.

# Links

Companion Volume Implementation Guides are available from VETNet - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=a53af4e4-b400-484e-b778-71c9e9d6aff2