# MEM18100 Fault-find, test and rectify AC machines and circuits

Release: 3

MEM18100 Fault-find, test and rectify AC machines and circuits

# Modification History

### Release 3. Prerequisite units updated

Release 2. Minor adjustments to reflect ERAC requirements for electrician licensing and revision of Essential Performance Capabilities

Release 1. New unit

# Application

This unit of competency has been developed for Engineering Tradesperson –industrial electrician apprenticeship training and the recognition of trade-level skills in locating and rectifying faults in alternating current (AC) machines and circuits.

It covers characteristics including their construction and operating principles. It also includes their application, control and protection methods, reversal of rotation and the requirements to limit starting current as well as skills in testing and fault finding, including abnormal operating conditions.

This unit covers the skills and knowledge required to meet the Electrical Regulatory Authorities Council (ERAC).

Essential Performance Capabilities (EPCs):

EPC 12 – Demonstrate the rationale and operating principles and characteristics of three phase induction motors and generators. Describe AS/NZS 3000 requirements and knowledge of local Supply Authority requirements for three phase motor installations and starters.

EPC 14 – Demonstrate knowledge of possible causes of malfunction of three phase induction motors and demonstrate the tests required for diagnosing faults.

EPC 15 – Describe the operating principles, characteristics, and suitability of typical control methods for single-phase motors and their key components.

### And

Essential Performance Capability (EPC) classified as ‘critical’:

EPC 13 – Demonstrate a knowledge of methods of electric motor selection, starting, connection and protection.

Some jurisdictions require the holder of this unit to be licensed or certified and users should check with the relevant authorities.

Band:	A

Unit Weight:	4

# Pre-requisite Unit

| MEM10016 | Terminate and test electrical wiring and accessories |
| --- | --- |
| MEM10018 | Select cable types and sizes to suit loads and electrical installation environment |
| MEM10019 | Select circuit protection devices by type and rating, fit to switchboards and install earthing |
| MEM10023 | Design and connect control switching of circuits for building services and industrial equipment |
| MEM12023 | Perform engineering measurements |
| MEM18001 | Use hand tools |
| MEM18104 | Dismantle, replace and assemble electrical components and equipment |

# Competency Field

Maintenance and diagnostics

# Elements and Performance Criteria

| Elements describe the essential outcomes. |  | Performance criteria describe the performance needed to demonstrate achievement of the element. |  |
| --- | --- | --- | --- |
| 1. | Determine job requirements | 1.1 | Follow standard operating procedures (SOPs) |
|  |  | 1.2 | Comply with work health and safety (WHS) requirements at all times, including appropriate risk control measures |
|  |  | 1.3 | Use appropriate personal protective equipment (PPE) in accordance with SOPs |
|  |  | 1.4 | Research the nature of the fault through checking of documentation and/or consultation with appropriate person |
| 2. | Prepare to fault find on AC machines and associated control circuits | 2.1 | Obtain all necessary tools, equipment and testing instruments needed to conduct fault diagnosis of AC machines and circuits |
|  |  | 2.2 | Isolate and tag circuits and equipment in accordance with procedures |
| 3. | Fault find AC machines and associated control circuits | 3.1 | Apply diagnostic techniques to solve problems in AC machines and their associated control circuits, including the use of specialised test equipment |
|  |  | 3.2 | Test single and three-phase windings for continuity and insulation resistance between windings and to earth with appropriate test equipment |
|  |  | 3.3 | Dismantle and reassemble AC machine using appropriate fitting techniques, equipment and tools in accordance with specifications and procedures, if required |
|  |  | 3.4 | Remove/repair/replace faulty components/circuits in accordance with manufacturer specifications and regulatory requirements |
|  |  | 3.5 | Test AC machine/circuit to ensure functionality in accordance with specifications |
|  |  | 3.6 | Document all necessary repairs in accordance with SOPs |

# Foundation Skills

This section describes those required skills (reading, writing, oral communication and numeracy) that are essential to workplace performance in this unit of competency.

Foundation skills essential to performance are explicit in the performance criteria of this unit of competency.

# Range of Conditions

| This field allows for different work environments and conditions that may affect performance. Essential operating conditions that may be present (depending on the work situation, needs of the candidate, accessibility of the item, and local industry and regional contexts) are included. |  |
| --- | --- |
| AC machines include three (3) or more of the following: | single-phase motors three-phase motors variable speed drives (VFDs) synchronous machines non-rotating AC equipment and components |
| Control starter circuits include one (1) or more of the following: | direct-on-line (DOL) star-delta autotransformer primary resistance secondary resistance |
| Split phase induction motors include: | split-phase motor capacitor-start motor capacitor-start, capacitor-run motor permanently-split capacitor motor shaded-pole motor |
| Environmental protection and general enclosure types include: | open motors protected motors drip-proof motors duct ventilated totally enclosed flameproof |
| Specialised test equipment includes one or more of the following: | built-in systems (software and site displays) vibration monitors infra-red temperature sensing device |
| Rotating electrical machines in general requirements include: | AS 1359.106-1996 Rotating electrical machines – General requirements – Methods of cooling (IC Code) |
| Regulatory requirements include: | AS/NZS 3000:2007 Electrical installations (known as the Australian/New Zealand Wiring Rules |
| Safe working practices include: | Demonstration of safe working practices and installation in accordance with industry established safe and sound practices |

# Unit Mapping Information

Release 2. Equivalent. Minor adjustments to reflect ERAC requirements for electrician licensing and revision of Essential Performance Capabilities.

# Links

Companion Volume implementation guides are found in VETNet - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=b7050d37-5fd0-4740-8f7d-3b7a49c10bb2

Assessment Requirements for MEM18100 Fault-find, test and rectify AC machines and circuits

# Modification History

### Release 3. Prerequisite units updated

Release 2. Minor adjustments to reflect ERAC requirements for electrician licensing and revision of Essential Performance Capabilities

Release 1. New unit

# Performance Evidence

Evidence required to demonstrate competence in this unit must be relevant to and satisfy the requirements of the elements and performance criteria on at least two (2) occasions and include:

following work instructions, standard operating procedures (SOPs) and safe work practices

identifying and interpreting circuits, drawings and specifications relevant to the work to be undertaken

determining the electrical and non-electrical isolation requirements to prevent the creation of hazards linked from the loss of machine/system/process control according to established procedures

using lock out tag procedures with appropriate tags/signs

proving electrical isolation and following established safety rules prior to working on electrical equipment or wiring

ensuring all electrical equipment and tools are tested and tagged and up to date

using specialised test equipment, including condition monitoring equipment to conduct on-line analysis

carrying out on-line functional tests for voltage and current using a voltmeter or multimeter and a clip on ammeter

applying fault finding and diagnostic techniques on at least three (3) or more of the following AC machines and circuits:

single-phase motors

three-phase motors

variable speed drives (VSDs)

synchronous machines

non-rotating AC equipment and components

carrying out electrical tests for continuity and insulation resistance tests; between windings and to earth of single and three-phase motors

dismantling, replacing and assembling single and three-phase AC machines using appropriate hand and power tools in accordance with manufacturer specifications, if required

complying with the Australian/New Zealand Wiring Rules and local supply requirements for three-phase motor installations and starters

using a synchroscope for paralleling of alternators

documenting all necessary repairs in accordance with SOPs.

# Knowledge Evidence

Evidence required to demonstrate the required knowledge for this unit must be relevant to and satisfy the requirements of the elements and performance criteria and include knowledge of:

safe work practices and procedures and use of personal protective equipment (PPE)

three-phase induction motors, including:

basic component parts of a three-phase induction motor, i.e. stator and rotor (squirrel-cage and wound rotor)

motor enclosures

terminal block arrangements – connecting a three-phase motor in both star and delta

operating principles, including:

rotating magnetic fields

rate of rotation and factors affecting it

direction of rotation and reversal

induction and its effects, including:

torque

slip

rotor frequency

operating characteristics, including:

squirrel-cage rotors

special purpose squirrel-cage rotors

wound-rotor motors

operating parameters for induction motors

single-phase induction motors, characteristics and operating principles of the following:

split-phase motor

capacitor-start motor

capacitor-start, capacitor-run motor

permanently-split capacitor motor

shaded-pole motor

series motor – operating characteristics and reversing the direction of rotation

comparison of single-phase and three-phase motors and advantages and disadvantages of three-phase motors

abnormal operating conditions for three-phase motors, including:

phase reversal, single phasing and overloading

voltage fluctuation, higher operating temperatures, frequency variation, overloading and frequent starting

other factors, including exposure to corrosive fumes, explosive vapours, dust, steam, salt air, high humidity, operation in ambient temperature of below approximately 100C or above 400C, or operation at altitudes in excess of 1000 metres

abnormal operating conditions for single-phase motors, including centrifugal switch failure

diagnostic techniques including the use of specialised test equipment, including growlers

electrical tests for continuity and insulation resistance tests; between windings and to earth of single and three-phase motors

testing, including the following:

DC test – to determine the stator resistance

no-load test – to determine the rotational losses and magnetisation current

locked rotor test – to determine the rotor and stator impedances

thermography and condition monitoring

dismantling three-phase motors, including application of ‘witness marks’

operation of a ’growler’ to perform voltage drop testing of armatures of the series or universal motor

electric motor control and protection, including:

reasons why motor protection is required

Australian/New Zealand Wiring Rules and local supply requirements for three-phase motor installations and starters, including:

isolation and switching

automatic starting

emergency stopping

starting methods for limitation of starting currents

three-phase motor starters and their operating principles and characteristics, including:

DOL

star-delta

autotransformer

primary resistance

secondary resistance

various types of motor overload protection, including high rupture capacity (HRC) fuses

operating principles of magnetically activated over-current relays, thermally activated over-current relays and combined thermal-magnetic over-current relays

temperature-dependent resistor protection

under-voltage and over-voltage protection

single-phasing and reverse-phase sequence protection and the protection methods

types of enclosures to give environmental protection, including:

open - ends of machine are open allowing free ventilation with fan attached to the motor shaft to draw air through the motor

protected - protection obtained by fastening steel wire mesh or perforated metal over enclosures with fan attached to the motor shaft to draw air through the motor

drip proof - an advance on the protected motors with openings further protected by a hood to prevent foreign materials or moisture from falling vertically into motor

duct ventilated - air is drawn from outside through a duct or air is forced via a blower through a duct to the motor

totally enclosed - no contact between the air outside and inside the machine can be classified as waterproof, weatherproof or submersible

flameproof - totally enclosed motor with additional precautions, including to seal bearings and used where there are flammable gases and risk of explosion if spark enters the atmosphere

AS 1359.106-1996 Rotating electrical machines – General requirements – Methods for cooling (IC Code)

three-phase motor braking and the principles of operation of the major types, including mechanical, eddy current, dynamic, regenerative and plug

altering the speed of AC induction motors by varying the number of poles or frequency

VSDs, including:

methods and operating principles

installation requirements

shielding and filtering

harmonics and power factor

performance characteristics

set up and commissioning

common faults – their symptoms and causes

three-phase synchronous machines – alternators:

construction and operating principles

excitation and generated voltage

effect of load on alternator voltage

effect of power factor on output voltage of an alternator

voltage regulation

alternator ratings expressed in kVA

parallel operation of alternators – synchronising and the methods used to achieve synchronisation, including the use of a synchroscope

effects of a change in excitation when connecting two alternators in parallel

three-phase synchronous machines – motors:

construction and operating principles

effect of a load on a synchronous motor

effect on varying the field (DC) excitation, including changes in power factor

hunting in three-phase synchronous machines and the methods used to reduce this effect, including the use of amortisseur windings in the pole faces of the rotor

starting methods and applications of three-phase synchronous motors

single-phase synchronous motors:

the primary purpose and the major types: reluctance and hysteresis motors

applications of single-phase synchronous motors

standby power supplies including uninterruptable power supplies (UPS) and the purpose they provide, i.e. mains power at a specified voltage and frequency

standby engine driven alternators starting methods and sequence of operation

non-rotating AC equipment and components including construction, operation and application of:

linear motors and actuators

solenoids, relays and contactors

welders and other non-rotating AC machines.

# Assessment Conditions

Assessors must:

have vocational competency in fault finding, testing and rectifying AC machines and circuits at least to the level being assessed with relevant industry knowledge and experience

satisfy the assessor requirements in the Standards for Registered Training Organisations 2015 and comply with the National Vocational Education and Training Regulator Act 2011 or equivalent legislation covering VET regulation in a non-referring State as the case requires.

Where possible assessment must occur in operational workplace situations. Where this is not possible or where personal safety or environmental damage are limiting factors, assessment must occur in a sufficiently rigorous simulated environment that reflects realistic operational workplace conditions. This must cover all aspects of workplace performance, including environment, task skills, task management skills, contingency management skills and job role environment skills.

Conditions for assessment must include access to all tools, equipment, materials and documentation required, including relevant workplace procedures, product and manufacturing specifications.

Assessment processes and techniques must be appropriate to the language, literacy and numeracy requirements of the work being performed and the needs of the candidate.

# Links

Companion Volume implementation guides are found in VETNet - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=b7050d37-5fd0-4740-8f7d-3b7a49c10bb2