# UEEHA0028 Perform compliance audits of hazardous areas and related electrical installation

Release: 1

UEEHA0028 Perform compliance audits of hazardous areas and related electrical installation

# Modification History

Release 1. This is the first release of this unit of competency in the Electrotechnology Training Package.

# Application

This unit involves the skills and knowledge required to conduct an audit of classified hazardous areas (e.g. where flammable gas or vapour hazards or explosive dust atmospheres and combustible dust layers have the potential to be, or are present), and the explosion-protection aspects of the related electrical installation, which include electrical, instrumentation, control and/or communications equipment and installations. It includes: reviewing the processes given for the hazardous area and its compatibility with the classification documentation held in the verification dossier; determining by the use of various tools or resources (e.g. construction or maintenance systems, facility documentation), or by inspection whether equipment or systems are compliant for the area in which they are installed including wiring systems; evaluating the currency of documentation held in the verification dossier; and reporting audit results, including recommendations for remediation of non-compliance and required updating of the verification dossier or documents that support the verification dossier. This unit applies to personnel required to audit areas that have been classified as hazardous in reference to AS/NZS60079.10.2 or equivalent. The auditing task itself would apply to the various lifecycle phases of an installation. It is appropriate for personnel that are required to complete some, or all, of the responsibilities required of ‘The Person with Executive Function’ (TPEF), as described in AS/NZS60079.17:2017, for example, where the continuous supervision maintenance strategy has been adopted, and there is a need to analyse or verify the effectiveness of the continuous supervision process. Site-specific work permits may be required to work in the hazardous environment. In addition, other permits may be required, such as confined space and to operate specific pieces of equipment such as elevated work platforms in various jurisdictions. Before any audit is planned, these conditions of control are to be considered. Additional and/or other conditions may apply in some jurisdictions subject to regulations related to electrical work. Practice in the workplace and during training is also subject to work health and safety (WHS)/occupational health and safety (OHS) regulations. This unit of competency and associated assessment requirements is adopted from clause 2.14 of AS/NZS 4761.1:2018 Competencies for working with electrical equipment for hazardous areas (EEHA). There may be differences between the content of this unit and AS/NZS 4761.1:2018, so the Standard must be checked to ensure compliance with it. Clause 2.14 of AS/NZS 4761.1:2018 also includes the following precondition for assessment: “A candidate seeking assessment in this unit shall have been deemed competent to audit compliance of electrotechnology systems at AQF level 4 or NZQF level 5 (BD) or equivalent.”

# Pre-requisite Unit

UEEHA0004 Enter a classified hazardous area to undertake work related to electrical equipment UEEHA0020 Conduct detailed inspection of electrical installations for hazardous areas UEEHA0022 Determine the explosion-protection requirements to meet a specified classified hazardous area UEEHA0038 Conduct visual and close inspection of electrical installations for hazardous areas

# Competency Field

Hazards

# Unit Sector

Electrotechnology

# Elements and Performance Criteria

| ELEMENTS |  | PERFORMANCE CRITERIA |  |
| --- | --- | --- | --- |
| Elements describe the essential outcomes. |  | Performance criteria describe the performance needed to demonstrate achievement of the element. |  |
| 1 | Prepare for and establish extent of the audit | 1.1 | Records system (verification dossier) is reviewed to verify that essential hazardous area documentation is retained and procedures for maintaining records are established |
|  |  | 1.2 | Hazardous area classification processes are applied to auditing classification and design documentation including the procedures followed and verifying traceability and authentication |
|  |  | 1.3 | Details of any alterations/modification to the plant or processes are ascertained from consultation with responsible plant personnel |
|  |  | 1.4 | Type and intended location of each item of equipment and routes of wiring systems subject to audit are determined from design drawings and documentation |
|  |  | 1.5 | WHS policies and procedures for working in the given hazardous area are obtained and interpreted |
|  |  | 1.6 | Compliant tools and equipment required for the audit are obtained and checked for correct operation and safety |
| 2 | Perform audit | 2.1 | WHS/OHS procedures, including compliance with requirements for isolation of explosion-protected equipment and circuits, are interpreted and applied |
|  |  | 2.2 | Area classification documentation is examined for compliance of process, traceability and relevance to the current plant and processes |
|  |  | 2.3 | Electrical design documents for the installation are assessed for compliance with the relevant standards and as-installed documentation |
|  |  | 2.4 | Certification documentation and any repair/overhaul or compliance assessment record for item of explosion-protected equipment are assessed for compliance with requirements for the current plant and processes |
|  |  | 2.5 | Appropriately authorised persons are directed to open equipment enclosures as required for the audit and on completion ensure integrity of explosion-protection is restored |
|  |  | 2.6 | Electrical equipment and installation are audited for conformance to the design as-installed specifications and compliance with requirements of the applicable standards |
|  |  | 2.7 | Inspection and maintenance records are evaluated against the condition of the plant and assessed for compliance with requirements |
| 3 | Report audit results | 3.1 | Differences between the hazardous area documentation (verification dossier), including the as-installed design specifications and installation, are reported |
|  |  | 3.2 | Deficiencies and inaccuracies in site record and non-conformances of explosion-protected equipment and the installation, and recommendation for their rectification, are documented in the audit report |
|  |  | 3.3 | The audit report is forwarded to the person responsible for actioning the recommendation/s |
|  |  | 3.4 | The audit report is forwarded to the person responsible for maintaining the hazardous area documentation (verification dossier) |

# Foundation Skills

Foundation skills essential to performance are explicit in the performance criteria of this unit of competency.

# Range of Conditions

| Range is restricted to essential operating conditions and any other variables essential to the work environment. Non-essential conditions may be found in the Electrotechnology Training Package Companion Volume Implementation Guide. |  |
| --- | --- |
| Essential operating conditions include: | an engineering office engaged in electrical design of electrical systems and installations for explosive atmospheres area classification documents installation design as-installed equipment inspection and maintenance records the hazardous area installation at the site and relevant authorised personnel |

# Unit Mapping Information

This is a new unit.

# Links

Companion Volume Implementation Guides are found in VETNet - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=b8a8f136-5421-4ce1-92e0-2b50341431b6