# UEERA0097 Install, commission, service and maintain variable refrigerant flow air conditioning systems

Release: 1

UEERA0097 Install, commission, service and maintain variable refrigerant flow air conditioning systems

# Modification History

Release 1. This is the first release of this unit of competency in the UEE Electrotechnology Training Package.

# Application

This unit involves the skills and knowledge required to safely and effectively install, commission, service and maintain variable refrigerant flow (VRF) air conditioning systems. It includes sourcing relevant data and schematics; installing components, pipe work, accessories and controls; commissioning the system to ensure it operates at the specified design conditions; locating and rectifying faults; and, carrying out maintenance tasks. VRF systems are commonly found in commercial applications. They contain one or more outdoor units with multiple indoor units. Each indoor unit typically has its own metering device and shares a common pipework system. They are either heat pump or heat recovery systems. Heat pump systems will only allow indoor units to operate in the same mode (either heating or cooling). A heat recovery system will allow each indoor unit to operate in a different mode (either heating or cooling) from the same system by the use of a branch box. The skills and knowledge in this unit of competency will be applied by refrigeration and air conditioning technicians during the installation, commissioning and servicing of VRF air conditioning systems. The skills and knowledge described in this unit require a current national Trainee or Full Refrigerant Handling Licence as it includes work on refrigeration and air conditioning equipment that carries the risk of a fluorocarbon refrigerant being emitted while decanting, manufacturing, installing, commissioning, servicing, maintaining or decommissioning activities are being carried out. Competency development activities in this unit are subject to regulations directly related to licensing. Where a licence or permit to practice is not held, skills and knowledge described in this unit require a relevant contract of training, such as an Australian Apprenticeship. Additional and/or other conditions may apply in some jurisdictions subject to regulations related to refrigeration, air conditioning and electrical work. Practice in the workplace and during training is also subject to work health and safety (WHS)/occupational health and safety (OHS) regulations.

# Pre-requisite Unit

UEECD0007 Apply work health and safety regulations, codes and practices in the workplace

UEERA0051 Install, commission, service and maintain air conditioning systems

# Competency Field

Refrigeration and air-conditioning

# Unit Sector

Electrotechnology

# Elements and Performance Criteria

| ELEMENTS |  | PERFORMANCE CRITERIA |  |
| --- | --- | --- | --- |
| Elements describe the essential outcomes. |  | Performance criteria describe the performance needed to demonstrate achievement of the element. |  |
| 1 | Prepare to work on variable refrigerant flow (VRF) air conditioning systems | 1.1 | WHS/OHS risk control measures and procedures for carrying out the work are obtained and implemented in accordance with workplace procedures and regulatory requirements |
|  |  | 1.2 | Work details are determined from documentation and/or supervisor to establish scope of work to be completed in accordance with workplace procedures |
|  |  | 1.3 | Relevant manufacturer specifications and worksite plans are interpreted and incorporated in work planning |
|  |  | 1.4 | Components, piping, accessories, controls and consumables for the work are obtained and checked against job requirements in accordance with Australian Standards and codes of practice |
|  |  | 1.5 | Tools, equipment and testing devices to complete work are obtained and checked for operational safety in accordance with workplace procedures |
| 2 | Install VRF air conditioning systems | 2.1 | The location and orientation of branching and support of pipe work is determined and laid out in accordance with system design |
|  |  | 2.2 | Major components are securely mounted in the locations identified by the documentation or the supervisor in accordance with workplace procedures and regulatory requirements |
|  |  | 2.3 | Refrigerant pipework and associated components are installed and tube cleanliness is maintained at all times in accordance with workplace procedures, Australian Standards and manufacturer specifications |
|  |  | 2.4 | Condensate pipework is installed and tested in accordance with design, Australian Standards and manufacturer specifications |
|  |  | 2.5 | Communication wiring is checked to ensure it conforms to manufacturer circuit diagram, specifications and Australian Standards |
|  |  | 2.6 | Pressure testing of the installed components and pipe work is conducted to the required level for the type of refrigerant being used in accordance with relevant Australian Standards, codes of practices and workplace procedures |
|  |  | 2.7 | Leaks are located and rectified employing appropriate methods in accordance with relevant Australian Standards, codes of practices and workplace procedures |
|  |  | 2.8 | Air conditioning system is evacuated to remove moisture and other contaminants in accordance with relevant Australian Standards, codes of practices and workplace procedures |
|  |  | 2.9 | Vacuum drop test is carried out to verify all moisture and other contaminants have been removed from the system in accordance with relevant Australian Standards, codes of practices and workplace procedures |
| 3 | Commission VRF air conditioning systems | 3.1 | Extra refrigerant charge quantity is documented in accordance with Australian Standards and manufacturer specifications |
|  |  | 3.2 | Measurements are obtained using manufacturer diagnostic tools and recorded to confirm system operation is in accordance with the system’s design and manufacturer specifications |
|  |  | 3.3 | Measurements are obtained and recorded to confirm that operating voltage and current are within manufacturer specifications |
| 4 | Locate and rectify faults on VRF air conditioning systems | 4.1 | Fault diagnosis processes are carried out in accordance with manufacturer processes and specifications, relevant Australian Standards, codes of practices and workplace procedures |
|  |  | 4.2 | Required repairs are identified and reported in accordance with manufacturer processes, relevant Australian Standards, codes of practices and workplace procedures |
|  |  | 4.3 | Routine maintenance requirements are identified in accordance with relevant Australian Standards and workplace procedures |
| 5 | Complete work and report activities | 5.1 | WHS/OHS risk control measures continue to be applied in accordance with workplace procedures and regulatory requirements |
|  |  | 5.2 | Worksite and equipment are cleaned and made safe in accordance with workplace procedures |
|  |  | 5.3 | Required documentation is completed in accordance with relevant regulations, Australian Standards and codes of practice |
|  |  | 5.4 | Supervisor is notified of task completion in accordance with workplace procedures |

# Foundation Skills

Foundation skills essential to performance are explicit in the performance criteria of this unit of competency.

# Range of Conditions

Range is restricted to essential operating conditions and any other variables essential to the work environment. Non-essential conditions may be found in the UEE Electrotechnology Training Package Companion Volume Implementation Guide.

# Unit Mapping Information

Newly created unit.

# Links

Companion Volume Implementation Guides are found in VETNet - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=b8a8f136-5421-4ce1-92e0-2b50341431b6