# UETDRTS002 Commission energy/revenue metering schemes

Release: 1

UETDRTS002 Commission energy/revenue metering schemes

# Modification History

Release 1. This is the first release of this unit of competency in the UET Transmission, Distribution and Rail Sector Training Package Release 2.0.

# Application

This unit covers the commissioning of energy/revenue metering schemes. This includes isolation, inspection, monitoring, testing, adjustment, repair, refurbishment and/or overhaul and functional checks of revenue metering schemes. It includes the requirements to prove the functionality of the metering scheme in accordance with electrical installation (state and national) standards, metrology procedures and compliance to tariff requirements. The application of the skills and knowledge described in this unit requires a licence/registration to practice in the workplace subject to regulations for undertaking of electrical work. Other conditions may apply under state and territory legislative and regulatory licensing requirements which must be confirmed prior to commencing this unit.

# Pre-requisite Unit

UEENEEE101A Apply Occupational Health and Safety regulations, codes and practices in the workplace UEENEEE102A Fabricate, assemble and dismantle utilities industry components UEENEEE104A Solve problems in d.c. circuits UEENEEE105A Fix and secure electrotechnology equipment UEENEEE107A Use drawings, diagrams, schedules, standards, codes and specifications UEENEEE137A Document and apply measures to control OHS risks associated with electrotechnology work UEENEEG006A Solve problems in single and three phase low voltage machines UEENEEG033A Solve problems in single and three phase low voltage electrical apparatus and circuits UEENEEG063A Arrange circuits, control and protection for general electrical installations UEENEEG076A Install and replace low voltage current transformer metering UEENEEG101A Solve problems in electromagnetic devices and related circuits UEENEEG102A Solve problems in low voltage a.c. circuits UEENEEG103A Install low voltage wiring and accessories UEENEEG104A Install appliances, switchgear and associated accessories for low voltage electrical installations UEENEEG105A Verify compliance and functionality of low voltage general electrical installations UEENEEG106A Terminate cables, cords and accessories for low voltage circuits UEENEEG107A Select wiring systems and cables for low voltage general electrical installations UEENEEG108A Trouble-shoot and repair faults in low voltage electrical apparatus and circuits UEENEEG109A Develop and connect electrical control circuits UEENEEG171A Install, set up and commission interval metering UETDREL001 Apply environmental requirements UETDREL005 Work safely in the vicinity of live electrical apparatus UETDRTS012 Install and replace complex energy/revenue metering schemes and associated equipment UETDRTS013 Install and replace high voltage metering and associated equipment UETDRTS016 Maintain compliance with national electricity market metrology practices and procedures UETDRTS020 Management of energy registration data errors for revenue billing purposes UETDRTS022 Perform current injection testing using phantom load UETDRTS024 Test and maintain energy/revenue metering schemes UETTDREL15 Respond to power systems technical enquiries and requests

# Competency Field

Testing

# Unit Sector

Not applicable.

# Elements and Performance Criteria

| ELEMENTS |  | PERFORMANCE CRITERIA |  |
| --- | --- | --- | --- |
| Elements describe the essential outcomes. |  | Performance criteria describe the performance needed to demonstrate achievement of the element. |  |
| 1 | Plan for the commissioning of energy/revenue metering schemes | 1.1 | Work health and safety (WHS)/occupational health and safety (OHS) practices/procedures and environmental and sustainable energy procedures, which may influence the commissioning of energy/revenue metering schemes, are reviewed and determined |
|  |  | 1.2 | Purpose of the commissioning of energy/revenue metering schemes is established after data is analysed and expected outcomes of the work are confirmed with appropriate personnel |
|  |  | 1.3 | Organisational established procedures, policies and specifications for the commissioning of energy/revenue metering schemes are obtained or established with appropriate personnel |
|  |  | 1.4 | Commissioning of energy/revenue metering schemes procedures are discussed with/directed to appropriate personnel in order to ascertain the project brief |
|  |  | 1.5 | Commissioning parameters are established from organisational established procedures, policies and specifications |
|  |  | 1.6 | Equipment/tools and personal protective equipment (PPE) are selected based on specified performance criteria and established procedures |
|  |  | 1.7 | Work roles and tasks are allocated according to requirements and individual competencies |
|  |  | 1.8 | Work is prioritised and sequenced for the most efficient/effective outcome, completed within an acceptable timeframe, to a quality standard and in accordance with established procedures |
|  |  | 1.9 | Liaison and communication issues with others/authorised personnel, authorities, clients and customers are resolved and activities coordinated to carry out work |
|  |  | 1.10 | Risk control measures are identified, prioritised and evaluated against the work schedule |
|  |  | 1.11 | Relevant internal/external work permits are obtained to coordinate the performance of work according to requirements and/or established procedures |
| 2 | Carry out the commissioning of energy/revenue metering schemes | 2.1 | WHS/OHS and sustainable energy principles, functionality and practices to prevent the incidents of accidents and minimise waste are incorporated into the project in accordance with requirements and/or established procedures |
|  |  | 2.2 | First aid, rescue and other related work procedures are performed according to requirements and/or established procedures |
|  |  | 2.3 | Lifting, climbing and use of power tools/equipment, techniques and practices are safely exercised according to requirements |
|  |  | 2.4 | Hazard warnings and safety signs are recognised and hazards and assessed WHS/OHS risks are reported to immediate authorised personnel for directions according to established procedures |
|  |  | 2.5 | Remedial actions are taken to overcome any shortfalls encountered in the work schedule according to requirements and/or established procedures |
|  |  | 2.6 | Testing equipment is used in accordance with the work schedule and requirements and/or established procedures |
|  |  | 2.7 | Commissioning of energy/revenue metering schemes is carried out in accordance with the work schedule |
|  |  | 2.8 | Technical advice is given regarding potential hazards, safety risks and control measures so that monitoring and preventative action can be undertaken and/or appropriate authorities consulted, where necessary, in accordance with requirements and established procedures |
|  |  | 2.9 | Essential knowledge and associated skills are applied in the safe commissioning of revenue metering schemes to ensure completion in an agreed timeframe according to requirements |
|  |  | 2.10 | Solutions to non-routine problems are identified and actioned, using essential knowledge and associated skills, according to requirements |
|  |  | 2.11 | Quality of work is monitored against personal performance agreement and/or established organisational and professional standards |
| 3 | Complete the commissioning of energy/revenue metering schemes | 3.1 | Final inspections of the commissioning of energy/revenue metering schemes using routine tests and acceptance tests are undertaken to ensure they comply with all requirements and include all specifications and documents needed to complete the project |
|  |  | 3.2 | Appropriate internal/external personnel are notified of completion and reports and/or completion documents are finalised/commissioned according to established procedures and timeframes |
|  |  | 3.3 | Reports and/or completion documents are submitted to relevant personnel/organisations for approval and, where applicable, statutory or regulatory approval |
|  |  | 3.4 | Approved copies of routine testing and acceptance testing procedures/activities/results, for the commissioning of energy/revenue metering schemes, documents are issued and records updated in accordance with established procedures |

# Foundation Skills

Foundation skills essential to performance are explicit in the performance criteria of this unit of competency.

# Range of Conditions

Range is restricted to essential operating conditions and any other variables essential to the work environment. Non-essential conditions may be found in the UET Transmission, Distribution and Rail Sector Training Package Companion Volume Implementation Guide.

# Unit Mapping Information

This unit replaces and is equivalent to UETTDRTS43 Commission energy/revenue metering schemes.

# Links

Companion Volume Implementation Guides are found in VETNet - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=229bace1-b7bc-4653-9300-dffb13ecfad7

Assessment Requirements for UETDRTS002 Commission energy/revenue metering schemes

# Modification History

Release 1. This is the first release of this unit of competency in the UET Transmission, Distribution and Rail Sector Training Package Release 2.0.

# Performance Evidence

Evidence required to demonstrate competence in this unit must be relevant to and satisfy all of the requirements of the elements and performance criteria on at least two separate occasions and include:

applying relevant work health and safety (WHS)/occupational health and safety (OHS) requirements, including the use of risk control measures applying sustainable energy principles and practices performing, on at least three (3) occasions, the commissioning of the following metering schemes types: single feeder high voltage (HV) low voltage (LV) current transformer customer sites performing, on at least three (3) occasions, commissioning involving at least seven (7) of the following: isolation inspection monitoring testing adjustment repair refurbishment and/or overhaul functional checks of revenue metering schemes demonstrating, on at least three (3) occasions, knowledge and application of at least two (2) different manufacturer’s: proprietary software application programming interrogations undertaking, on at least three (3) occasions, the following: calculations, including obtain final revenue multiplier validation of meter pulse multiplier dealing with unplanned events on at least one (1) occasion.

# Knowledge Evidence

Evidence required to demonstrate competence in this unit must be relevant to and satisfy all of the requirements of the elements and performance criteria and include knowledge of:

commissioning techniques evaluation of the metering design and equipment accuracy to ensure suitability with national electricity market requirements recording nameplate details for all metering scheme components and ensuring compliance with the design accuracy class confirmation of instrument transformer connected ratios, polarities, burdens and voltage drops checking integrity of all wiring, connections and terminalisations ensuring cable types and sizes selected are correct phase sequence and vector relationships are correct documentation verifying the errors of current transformers and voltage transformers validation of meter data to verify the metering programming parameters, display and error functions are all correct in accordance with manufacturer specifications verifying meter programming to ensure the best possible resolution of energy data measurement and recording validating the interval data with the responsible person and/or meter data provider confirming remote communications with the metering is established and is of sufficient quality to support reliable communications and data transfer standards, codes, Commonwealth/state/territory legislation, supply authority regulations and/or enterprise requirements associated with the commissioning procedures requirements for the use of isolation and tagging, manuals, system diagrams/plans and drawings requirements for the use of maintenance and commissioning manuals, system diagrams/plans and drawings techniques in commissioning procedures – planning, policy and testing techniques close out requirements requirements for the use of meter manufacturer manuals, system diagrams/plans and drawings.

# Assessment Conditions

Assessors must hold credentials specified within the Standards for Registered Training Organisations current at the time of assessment. Assessment must satisfy the Principles of Assessment and Rules of Evidence and all regulatory requirements included within the Standards for Registered Training Organisations current at the time of assessment. Assessment must occur in workplace operational situations where it is appropriate to do so; where this is not appropriate, assessment must occur in simulated conditions involving realistic and authentic activities that replicate operational workplace conditions. Assessment processes and techniques must be appropriate to the language, literacy and numeracy requirements of the work being performed and the needs of the candidate. Resources for assessment must include access to: a range of relevant exercises, case studies and/or other simulations relevant and appropriate materials, tools, facilities, equipment and personal protective equipment (PPE) currently used in industry applicable documentation, including workplace procedures, relevant industry standards, equipment specifications, regulations, codes of practice and operation manuals.

# Links

Companion Volume Implementation Guides are found in VETNet - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=229bace1-b7bc-4653-9300-dffb13ecfad7