# UETDRTS025 Test and maintain energy/revenue metering schemes (complex)

Release: 1

UETDRTS025 Test and maintain energy/revenue metering schemes (complex)

# Modification History

Release 1. This is the first release of this unit of competency in the UET Transmission, Distribution and Rail Sector Training Package Release 2.0.

# Application

This unit covers the testing and maintenance of energy/revenue metering schemes in complex situations. Complex metering schemes include summation, subtraction, generation, bulk supply, interconnector and wholesale metering installations. Testing and maintenance include isolation, accuracy testing, inspection, monitoring, adjustment, repair or overhaul and functional checks of complex energy/revenue metering schemes. It includes the requirements to prove the functionality of the metering scheme in accordance with electrical installation (state/territory and national) standards, metrology procedures and compliance to tariff requirements. This also includes the identification of faults with metering equipment, energy registration and revenue billing in accordance with established procedures. The application of the skills and knowledge described in this unit requires a licence/registration to practice in the workplace subject to regulations for undertaking of electrical work. Other conditions may apply under state and territory legislative and regulatory licensing requirements which must be confirmed prior to commencing this unit.

# Pre-requisite Unit

UEENEED104A Use engineering applications software on personal computers UEENEEE101A Apply Occupational Health and Safety regulations, codes and practices in the workplace UEENEEE102A Fabricate, assemble and dismantle utilities industry components UEENEEE104A Solve problems in d.c. circuits UEENEEE105A Fix and secure electrotechnology equipment UEENEEE107A Use drawings, diagrams, schedules, standards, codes and specifications UEENEEE124A Compile and produce an energy sector detailed report UEENEEE125A Provide engineering solutions for problems in complex multiple path circuits UEENEEE126A Provide solutions to basic engineering computational problems UEENEEE137A Document and apply measures to control OHS risks associated with electrotechnology work UEENEEG006A Solve problems in single and three phase low voltage machines UEENEEG033A Solve problems in single and three phase low voltage electrical apparatus and circuits UEENEEG063A Arrange circuits, control and protection for general electrical installations UEENEEG076A Install and replace low voltage current transformer metering UEENEEG101A Solve problems in electromagnetic devices and related circuits UEENEEG102A Solve problems in low voltage a.c. circuits UEENEEG103A Install low voltage wiring and accessories UEENEEG104A Install appliances, switchgear and associated accessories for low voltage electrical installations UEENEEG105A Verify compliance and functionality of low voltage general electrical installations UEENEEG106A Terminate cables, cords and accessories for low voltage circuits UEENEEG107A Select wiring systems and cables for low voltage general electrical installations UEENEEG108A Trouble-shoot and repair faults in low voltage electrical apparatus and circuits UEENEEG109A Develop and connect electrical control circuits UEENEEG149A Provide engineering solutions to problems in complex polyphase power circuits UEENEEG171A Install, set up and commission interval metering UETDREL001 Apply environmental requirements UETDREL005 Work safely in the vicinity of live electrical apparatus UETDRIS005 Implement & monitor power system environmental & sustainable energy management policies & procedures UETDRIS006 Implement and monitor the power system organisational WHS/OHS policies, procedures and programs UETDRTS002 Commission energy/revenue metering schemes UETDRTS012 Install and replace complex energy/revenue metering schemes and associated equipment UETDRTS013 Install and replace high voltage metering and associated equipment UETDRTS016 Maintain compliance with national electricity market metrology practices and procedures UETDRTS020 Management of energy registration data errors for revenue billing purposes UETDRTS022 Perform current injection testing using phantom load UETDRTS024 Test and maintain energy/revenue metering schemes UETTDREL15 Respond to power systems technical enquiries and requests

# Competency Field

Testing

# Unit Sector

Not applicable.

# Elements and Performance Criteria

| ELEMENTS |  | PERFORMANCE CRITERIA |  |
| --- | --- | --- | --- |
| Elements describe the essential outcomes. |  | Performance criteria describe the performance needed to demonstrate achievement of the element. |  |
| 1 | Plan for the testing and maintenance of energy/revenue metering schemes (complex) | 1.1 | Work health and safety (WHS)/occupational health and safety (OHS) practices/procedures and environmental and sustainable energy procedures, which may influence the testing and maintenance of energy/revenue metering schemes (complex), are reviewed and determined |
|  |  | 1.2 | Purpose of testing and maintenance of energy/revenue metering schemes (complex) is established after data is analysed and expected outcomes of the work are confirmed with appropriate personnel |
|  |  | 1.3 | Organisational established procedures, policies and specifications for the testing and maintenance of energy/revenue metering schemes (complex) are obtained or established with appropriate personnel |
|  |  | 1.4 | Testing and maintenance of energy/revenue metering schemes (complex) procedures are discussed with/directed to appropriate personnel in order to ascertain the project brief |
|  |  | 1.5 | Testing and maintenance parameters are established from organisational established procedures, policies and specifications |
|  |  | 1.6 | Equipment/tools and personal protective equipment (PPE) are selected based on specified performance criteria and established procedures |
|  |  | 1.7 | Work roles and tasks are allocated according to requirements and individual competencies |
|  |  | 1.8 | Work is prioritised and sequenced for the most efficient/effective outcome, completed within an acceptable timeframe, to a quality standard and in accordance with established procedures |
|  |  | 1.9 | Liaison and communication issues with others/authorised personnel, authorities, clients and customers are resolved and activities coordinated to carry out work |
|  |  | 1.10 | Risk control measures are identified, prioritised and evaluated against the work schedule |
|  |  | 1.11 | Relevant internal/external work permits are obtained to coordinate the performance of work according to requirements and/or established procedures |
| 2 | Carry out the testing and maintenance of energy/revenue metering schemes (complex) | 2.1 | WHS/OHS and sustainable energy principles, functionality and practices to prevent the incidents of accidents and minimise waste are incorporated into the project in accordance with requirements and/or established procedures |
|  |  | 2.2 | First aid, rescue and other related work procedures are performed according to requirements and/or established procedures |
|  |  | 2.3 | Lifting, climbing and use of power tools/equipment, techniques and practices are safely exercised according to requirements |
|  |  | 2.4 | Hazard warnings and safety signs are recognised and hazards and assessed WHS/OHS risks are reported to immediate authorised personnel for directions according to established procedures |
|  |  | 2.5 | Remedial actions are taken to overcome any shortfalls encountered in the work schedule according to requirements and/or established procedures |
|  |  | 2.6 | Testing equipment is used in accordance with the work schedule and requirements and/or established procedures |
|  |  | 2.7 | Routine testing and acceptance testing of the testing and maintenance of energy/revenue metering schemes (complex) are carried out in accordance with the work schedule |
|  |  | 2.8 | Technical advice is given regarding potential hazards, safety risks and control measures so that monitoring and preventative action can be undertaken and/or appropriate authorities consulted, where necessary, in accordance with requirements and established procedures |
|  |  | 2.9 | Essential knowledge and associated skills are applied in the safe testing and maintenance of energy/revenue metering schemes (complex) to ensure completion in an agreed timeframe according to requirements |
|  |  | 2.10 | Solutions to non-routine problems are identified and actioned, using essential knowledge and associated skills, according to requirements |
|  |  | 2.11 | Quality of work is monitored against personal performance agreement and/or established organisational and professional standards |
| 3 | Complete the testing and maintenance of energy/revenue metering schemes (complex) | 3.1 | Final inspections of the testing and maintenance of energy/revenue metering schemes (complex) using routine tests and acceptance tests are undertaken to ensure they comply with all requirements and include all specifications and documents needed to complete the project |
|  |  | 3.2 | Appropriate internal/external personnel are notified of completion and reports and/or completion documents are finalised/commissioned according to established procedures and timeframes |
|  |  | 3.3 | Reports and/or completion documents are submitted to relevant personnel/organisations for approval and, where applicable, statutory or regulatory approval |
|  |  | 3.4 | Approved copies of routine testing and acceptance testing procedures/activities/results, for the testing and maintenance of energy/revenue metering schemes (complex), documents are issued and records updated in accordance with established procedures |

# Foundation Skills

Foundation skills essential to performance are explicit in the performance criteria of this unit of competency.

# Range of Conditions

Range is restricted to essential operating conditions and any other variables essential to the work environment. Non-essential conditions may be found in the UET Transmission, Distribution and Rail Sector Training Package Companion Volume Implementation Guide.

# Unit Mapping Information

This unit replaces and is equivalent to UETTDRTS44 Test and maintain energy/revenue metering schemes (complex).

# Links

Companion Volume Implementation Guides are found in VETNet - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=229bace1-b7bc-4653-9300-dffb13ecfad7