# UETTDRTS47 Commission energy/revenue metering schemes (complex)

Release: 1

UETTDRTS47 Commission energy/revenue metering schemes (complex)

# Modification History

Release 1. This is the first release of this unit of competency in the UET Transmission, Distribution and Rail Sector Training Package.

# Application

This unit covers the commissioning of energy/revenue metering schemes in complex situations, including summation, subtraction, generation, bulk supply, interconnector and wholesale metering installations. This includes isolation, inspection, monitoring, testing, adjustment, repair, refurbishment and/or overhaul and functional checks of complex revenue metering schemes. It includes the requirements to prove the functionality of the metering scheme in accordance with electrical installation (state and national) standards, metrology procedures and compliance to tariff requirements. The application of the skills and knowledge described in this unit requires a licence/registration to practice in the workplace subject to regulations for undertaking of electrical work. Other conditions may apply under state and territory legislative and regulatory licencing requirements which must be confirmed prior to commencing this unit.

# Pre-requisite Unit

Common Unit Group UEENEED104A Use engineering applications software on personal computers UEENEEE101A Apply Occupational Health and Safety regulations, codes and practices in the workplace UEENEEE102A Fabricate, assemble and dismantle utilities industry components UEENEEE104A Solve problems in d.c. circuits UEENEEE105A Fix and secure electrotechnology equipment UEENEEE107A Use drawings, diagrams, schedules, standards, codes and specifications UEENEEE124A Compile and produce an energy sector detailed report UEENEEE125A Provide engineering solutions for problems in complex multiple path circuits UEENEEE126A Provide solutions to basic engineering computational problems UEENEEE137A Document and apply measures to control OHS risks associated with electrotechnology work UEENEEG006A Solve problems in single and three phase low voltage machines UEENEEG033A Solve problems in single and three phase low voltage electrical apparatus and circuits UEENEEG063A Arrange circuits, control and protection for general electrical installations UEENEEG076A Install and replace low voltage current transformer metering UEENEEG101A Solve problems in electromagnetic devices and related circuits UEENEEG102A Solve problems in low voltage a.c. circuits UEENEEG103A Install low voltage wiring and accessories UEENEEG104A Install appliances, switchgear and associated accessories for low voltage electrical installations UEENEEG105A Verify compliance and functionality of low voltage general electrical installations UEENEEG106A Terminate cables, cords and accessories for low voltage circuits UEENEEG107A Select wiring systems and cables for low voltage general electrical installations UEENEEG108A Trouble-shoot and repair faults in low voltage electrical apparatus and circuits UEENEEG109A Develop and connect electrical control circuits UEENEEG149A Provide engineering solutions to problems in complex polyphase power circuits UEENEEG171A Install, set up and commission interval metering UETTDREL11 Apply sustainable energy and environmental procedures UETTDREL15 Respond to power systems technical enquiries and requests UETTDREL16 Working safely near live electrical apparatus UETTDRIS62 Implement and monitor the power system organisational WHS/OHS policies, procedures and programs UETTDRIS63 Implement & monitor power system environmental & sustainable energy management policies & procedures UETTDRTS37 Perform current injection testing using phantom load UETTDRTS38 Install and replace high voltage metering and associated equipment UETTDRTS39 Maintain compliance with national electricity market metrology practices and procedures UETTDRTS40 Test and maintain energy/revenue metering schemes UETTDRTS41 Install and replace complex energy/revenue metering schemes and associated equipment UETTDRTS42 Management of energy registration data errors for revenue billing purposes UETTDRTS43 Commission energy/revenue metering schemes UETTDRTS44 Test and maintain energy/revenue metering schemes (complex)

# Competency Field

Testing

# Unit Sector

Not applicable.

# Elements and Performance Criteria

| ELEMENTS |  | PERFORMANCE CRITERIA |  |
| --- | --- | --- | --- |
| Elements describe the essential outcomes. |  | Performance criteria describe the performance needed to demonstrate achievement of the element. |  |
| 1 | Plan for the commissioning of energy/revenue metering schemes (complex) | 1.1 | Work health and safety (WHS)/occupational health and safety (OHS) practices/procedures and environmental and sustainable energy procedures, which may influence the commissioning of energy/revenue metering schemes (complex), are reviewed and determined |
|  |  | 1.2 | Purpose of the commissioning of energy/revenue metering schemes (complex) is established after data is analysed and expected outcomes of the work are confirmed with appropriate personnel |
|  |  | 1.3 | Organisational established procedures, policies and specifications for the commissioning of energy/revenue metering schemes (complex) are obtained or established with appropriate personnel |
|  |  | 1.4 | Commissioning of energy/revenue metering schemes (complex) procedures are discussed with/directed to appropriate personnel in order to ascertain the project brief |
|  |  | 1.5 | Commissioning parameters are established from organisational established procedures, policies and specifications |
|  |  | 1.6 | Equipment/tools and personal protective equipment (PPE) are selected based on specified performance criteria and established procedures |
|  |  | 1.7 | Work roles and tasks are allocated according to requirements and individual competencies |
|  |  | 1.8 | Work is prioritised and sequenced for the most efficient/effective outcome, completed within an acceptable timeframe, to a quality standard and in accordance with established procedures |
|  |  | 1.9 | Liaison and communication issues with others/authorised personnel, authorities, clients and customers are resolved and activities coordinated to carry out work |
|  |  | 1.10 | Risk control measures are identified, prioritised and evaluated against the work schedule |
|  |  | 1.11 | Relevant internal/external work permits are obtained to coordinate the performance of work according to requirements and/or established procedures |
| 2 | Carry out the commissioning of energy/revenue metering schemes (complex) | 2.1 | WHS/OHS and sustainable energy principles, functionality and practices to prevent the incidents of accidents and minimise waste are incorporated into the project in accordance with requirements and/or established procedures |
|  |  | 2.2 | First aid, rescue and other related work procedures are performed according to requirements and/or established procedures |
|  |  | 2.3 | Lifting, climbing and use of power tools/equipment, techniques and practices are safely exercised according to requirements |
|  |  | 2.4 | Hazard warnings and safety signs are recognised and hazards and assessed WHS/OHS risks are reported to immediate authorised personnel for directions according to established procedures |
|  |  | 2.5 | Remedial actions are taken to overcome any shortfalls encountered in the work schedule according to requirements and/or established procedures |
|  |  | 2.6 | Testing equipment is used in accordance with the work schedule and requirements and/or established procedures |
|  |  | 2.7 | Commissioning of energy/revenue metering schemes (complex) is carried out in accordance with the work schedule |
|  |  | 2.8 | Technical advice is given regarding potential hazards, safety risks and control measures so that monitoring and preventative action can be undertaken and/or appropriate authorities consulted, where necessary, in accordance with requirements and established procedures |
|  |  | 2.9 | Essential knowledge and associated skills are applied in the safe commissioning of energy/revenue metering schemes (complex) to ensure completion in an agreed timeframe according to requirements |
|  |  | 2.10 | Solutions to non-routine problems are identified and actioned, using essential knowledge and associated skills, according to requirements |
|  |  | 2.11 | Quality of work is monitored against personal performance agreement and/or established organisational and professional standards |
| 3 | Complete the commissioning of energy/revenue metering schemes (complex) | 3.1 | Final inspections of the commissioning of energy/revenue metering schemes (complex) using routine tests and acceptance tests are undertaken to ensure they comply with all requirements and include all specifications and documents needed to complete the project |
|  |  | 3.2 | Appropriate internal/external personnel are notified of completion and reports and/or completion documents are finalised/commissioned according to established procedures and timeframes |
|  |  | 3.3 | Reports and/or completion documents are submitted to relevant personnel/organisations for approval and, where applicable, statutory or regulatory approval |
|  |  | 3.4 | Approved copies of routine testing and acceptance testing procedures/activities/results, for the commissioning of energy/revenue metering schemes (complex), documents are issued and records updated in accordance with established procedures |

# Foundation Skills

Foundation skills essential to performance are explicit in the performance criteria of this unit of competency.

# Range of Conditions

Range is restricted to essential operating conditions and any other variables essential to the work environment. Non-essential conditions may be found in the Companion Volume Implementation Guide.

# Unit Mapping Information

This unit replaces and is equivalent to UETTDRTS47A Commission energy/revenue metering schemes (complex).

# Links

UET Training Package Companion Volume Implementation Guide is found in VETNet - https://vetnet.gov.au/Pages/TrainingDocs.aspx?q=229bace1-b7bc-4653-9300-dffb13ecfad7